## Sheet1
S. No. | Description (Equipment Name) | Unit Rating (kW) | Quantity | Total Connected Load (kW) | Diversity Factor (%) | Maximum Demand (kW) | NOTE
PART A: RESIDENTIAL LOAD (Flats)
1 | Standard 3BHK Flat Load (Lights, Fans, Sockets) | 5 | 40 | 200 | 50 | 100
2 | VRV Air Conditioning (Indoor + Outdoor Units) | 6 | 40 | 240 | 60 | 144
3 | Geysers & Heavy Appliances | 3 | 40 | 120 | 40 | 48
TOTAL RESIDENTIAL LOAD |  |  |  | 560 |  | 292
PART B: COMMON AREA SERVICES
4 | Schindler Passenger Lift (High Speed) | 7 | 2 | 14 | 100 | 14
5 | Water Transfer Pumps (Domestic) | 7.5 | 2 | 15 | 50 | 7.5
6 | Common Area Lighting (LED) | 5 | 1 | 5 | 100 | 5
7 | External/Landscape Lighting | 4 | 1 | 4 | 100 | 4
8 | EV Charging Stations | 7.4 | 5 | 37 | 40 | 14.8
9 | STP (Sewage Treatment Plant) | 10 | 1 | 10 | 100 | 10
TOTAL COMMON LOAD |  |  |  | 85 |  | 55.3
PART C: CRITICAL / FIRE SERVICES
10 | Main Fire Pump | 55 | 1 | 55 |  |  | Only runs during Fire
11 | Jockey Pump | 5.5 | 1 | 5.5 |  |  | Maintains pressure
12 | Staircase Pressurization Fan | 7.5 | 2 | 7.5 |  |  | Smoke control
PARAMETER | VALUE | UNIT
Total Connected Load | 645 | KW
Total Max Demand (P) | 347.3 | KW
Power Factor (PF) | 0.8 | KW
Calculated kVA (P/PF) | 434.125 | KW
Safety Margin | 14 | KW
Final Transformer Capacity | 520.95 | KW
Selected Standard Rating | 630 | KW

## Sheet2
Level | Component Name | Rating | Quantity | Note | Column1
Source | Transformer | 630 kVA | 1 | Outdoor
Source | DG Set (Backup) | 250 kVA | 1 | Acoustic Enclosure
Main Panel | Main LT Panel (PCC) | 1000 A | 1 | With ATS (Auto Switch)
Riser | Main Busbar (BBT) | 800 A | 40 Meters | G to Terrace Height
Floors | Tap-off Box | 63 A | 10 | 1 per Floor
Floors | Meter Board | 0 | 10 | 4 Meters inside
Final | Flat DB | 8 Way TPN | 40 | Inside Flats

## Bill_of_Quantities_BoQ
S.No. | Item Description | Unit | Quantity | Rate (₹) | Amount (₹)
1 | Transformer: 630 kVA, 11/0.433 kV, Oil Cooled Type | Nos. | 1 | 950000 | 950000
2 | Diesel Generator (DG Set): 250 kVA, Silent Enclosure, Auto-Start | Nos. | 1 | 1400000 | 1400000
3 | Main LT Panel: Floor mounted, with 1000A ACB Incomer & Busbar coupler | Nos. | 1 | 450000 | 450000
4 | Capacitor Bank (APFC): 250 kVAR | Nos. | 1 | 180000 | 180000
5 | Rising Mains (BBT): 800A, 4-Pole Aluminium Busbar Trunking | Mtrs. | 45 | 9500 | 427500
6 | Tap-off Box: Plug-in unit for BBT with 125A MCCB | Nos. | 10 | 18000 | 180000
7 | Floor Distribution Panel: Wall mounted, for 4 Flats metering | Nos. | 10 | 35000 | 350000
8 | Energy Meters: Single Phase Digital kWh Meter | Nos. | 40 | 2500 | 100000
9 | Sub-main Cable: 4C x 16 sq.mm Al. Armoured Cable (Floor Panel to Flat DB) | Mtrs. | 600 | 350 | 210000
10 | Earthing: Copper Plate Earthing Set | Sets | 4 | 8000 | 32000
|  |  |  | Total Project Cost= | 4279500